## About
BGDPbES BAU Guaranteed Dispatch Percentage by Electricity Source | Alabama | 2026-09-02 | Alabama | AL
Active state: cell B1 (full state name). B2 resolves the abbreviation used by the calc tabs. | AL |  | Arizona | AZ
|  |  | Arkansas | AR
Purpose: | Guarantee a portion of coal dispatch. EPS under-dispatches coal ~-27% nationally vs EIA-923 2025 (gas +3.4%) because annual-average least-cost dispatch cannot represent the non-price factors that kept the real coal fleet at ~50% CF (seasonal gas price spikes hidden by the annual average, utility self-scheduling, coal supply contracts, minimum-run and pipeline constraints). The BFPaT electricity-sector fuel prices were audited 2026-07-22 and are correct (EIA EPA 7.17/7.20 2024 anchors x CPI-U 2012$ deflator, STEO Jun-2026 2025 step of gas x1.41 / coal x0.98), so the calibration lever is guaranteed dispatch, not prices. |  | California | CA
Mechanism: | Guaranteed dispatch = capacity x expected hourly CF x BGDPbES, per hour (proportionally scaled back only if hourly demand is exceeded); the remaining capacity still bids into RPS and least-cost dispatch, up to the full expected CF. Because HYECFCA anchors start-year expected CFs to 2025 observed CFs, BGDPbES[coal]=X floors start-year coal generation at X x (2025 observed generation) while leaving (1-X) to economics. |  | Colorado | CO
Layout (2026-08-21): | Every output value flows from exactly two tabs. `Defaults` holds ONE value per tech -- the value used for every state with no calibrated override (builder constants, with a note per tech). `Tuned` holds the long-format state¦tech calibrated overrides: the per-state coal/gas guarantees from the tuning-results CSV (qc/bgd_tune_results_merged_2026-08-14.csv), the peaker exceptions (MT/ND/VA/WA/WV), and the hydro exceptions (SD 0.75, WA 0.0). The output formula is IFERROR(Tuned lookup, Defaults lookup), plus the Keys pin table (2025-only), the hydro cap, and the VT hydro ramp. The former Current_BGDPbES tab (deployed CSVs compiled verbatim) was REMOVED: it made every rebuild re-import whatever was deployed, so hand decisions could be silently overwritten. Tuning passes cannot overwrite Defaults-driven rows -- the probe/tune scripts patch only their named coal/gas/peaker row in the run tree (and restore it), and the results CSVs carry only the five g_* columns. |  | Connecticut | CT
Zeroed techs (2026-08-21): | Six never-built techs are ZERO in every year and every state (Olivia): hard coal w CCS, natural gas combined cycle w CCS, biomass w CCS, lignite w CCS, small modular reactor, hydrogen combined cycle. Their previous values (0.15/0.15/1.0/1.0/0.0/1.0) were inherited verbatim from the eps-us national template, never a state calibration, and a nonzero guarantee on a tech EPS may BUILD in a policy scenario forces that new capacity to run near must-run from its first year, ahead of least-cost dispatch. Hydrogen combustion turbine is deliberately NOT zeroed and keeps its 1.0. |  | Delaware | DE
Values: | The four coal/gas rows (hard coal, lignite, NG steam turbine, NGCC) are 2025-ONLY (Olivia 2026-08-17): zero in every year except 2025, where each state takes its pin-table value if pinned, else its Tuned value, else the Defaults value (0 = no floor). After the calibrated start year the model determines its own coal/gas mix. The tuned values are the Phase C pass (2026-08-14, coal/gas balance on climate-0813: EQUAL relative error on coal and gas given the demand level, price gate <=5%), with earlier passes carried forward for untouched states. Hydro keeps the flat 0.90 convention; NG peaker keeps its flat per-state values (structural convention, not calibration). |  | Florida | FL
VT hydro ramp: | VT hydro = the Keys-tab F:G ramp block (Keys hydro_ramp_state, calibrated 2026-08-11): 0 through 2025, 0.3/0.5/0.7/0.85 over 2026-29, 0.9 from 2030. VT hydro dispatch otherwise collapses post-2025 in BAU and ClimateAmbition (must-take builds saturate the fixed requirement and wholesale falls to ~$0-9/MWh, below any defensible HOC); the ramp floors it at ~1.0 TWh BAU / >=0.78 TWh ClimateAmbition while leaving 2025 dispatch and prices byte-identical to the current calibration. A flat guarantee was tested and rejected (reorders 2025: guaranteed dispatch runs ahead of the RPS pass, g=0.7 pushed wind -22% vs observed); so was HOC 35 (zero dispatch effect, 2025 wholesale -15%). Evidence: docs/findings/vt-hydro-guarantee-ramp-2026-08-11.md. |  | Georgia | GA
Hydro guarantee cap (2026-08-13): | Olivia set a standing MAX of 0.90 on BGDPbES[hydro] -- no state should reach 1.0, because a near-must-run hydro fleet is removed from marginal price formation. ID was the only state above the cap (1.0) and is now 0.90. That value was LOAD-BEARING, not decorative: removing it alone moved ID hydro +1.94% -> -7.18% vs EIA-923 2025, so it was PAIRED with HOC 80 -> 35, which recovers it to +1.30% (price gate PASS). SD is deliberately LEFT at 0.75 -- raising it to 0.90 pinned SD hydro at +10.45% (= 0.90 x SD potential 4.633, above its EIA benchmark), and 0.75 already satisfies the cap. GENERAL LESSON: the guarantee denominator is the state hydro POTENTIAL, not the EIA benchmark, so "EPS/EIA > guarantee" does NOT prove a guarantee is non-binding -- test by running it. WA (0.0) and VT (ramp) keep their documented exceptions. Evidence: docs/findings/start-year-dispatch-calibration-2026-08-13.md. |  | Idaho | ID
2025 pin table (2026-08-17): | Twelve state¦tech guarantees are overridden in 2025 ONLY (Keys I:J pin table + pin_year; the output-tab year formula applies them). Two Olivia decisions merged: (1) WA hard coal 0.947 / NGCC 0.795 — the US_ClimateAmbition scenario shifts ~6 TWh of WA start-year dispatch from gas into hydro at the same $40 HOC, and 2025 is history, so observed dispatch is pinned; from 2026 policy hydro flexes freely (75.9 TWh in 2026, inside WA's 60.7-91.8 TWh 2010-24 range). (2) The option-B coal/gas retune ("equal % error on coal and gas, given the demand level"): MT/AZ/IL/IA/SC/WY hard-coal, KS/CO/MN NGCC, ND peaker (ND has no NGCC fleet — its NGCC floor was measured inert). Spreads closed to <=1.6pp everywhere except WY (4.0pp, price-gate-limited). Pins, not flat floors, because the 2025 response is identical while flat floors carry measured late-year price costs (WY ~29%, MN ~21% industry 2050). Evidence: qc/bgd_tune_results_optionb*_2026-08-17.csv, docs/findings/wa-2025-guarantee-pin-2026-08-17.md. |  | Illinois | IL
Hydro 2025 pins (2026-08-24): | Twelve hydro crowd-out states get a 2025-ONLY hydro pin (Keys I:J) at g = EIA-923-2025 target / expected output, paired with HOC 62 (NV 45; NV needs no pin -- its 0.9 floor already equals its target). Mechanism: the 2025-only coal/gas guarantees expire in 2026 and hydro at a low HOC under-prices carbon-loaded/forecast-priced fossil, jumping to its availability on flat capacity (AL +121%, AZ +174%, NV +205% vs target over 2026-29 on climate-0824). The pin holds 2025 exact (probes: -0.0% in 11 states, SD -0.5%) with no wind/solar displacement (SD mildest exception, -4%), and the raised HOC returns 2026+ dispatch to economics: hydro lands on its 0.9 out-year floor (-1% to -17% vs target) and fossil recovers (CA gas 2026: 49 -> 76 TWh). Pins may exceed the 0.90 cap in the pin year ONLY (Olivia direction 2026-08-24). OR joined the pinned set by Olivia decision same day (pin 0.9707 = target/expected 29.564, + HOC 62): the fix makes all four OR generation series realistic (hydro flat ~27-28 TWh, gas glides per HB 2021, wind/solar build more) with 2025-26 retail unchanged; 2028-29 retail +7-13% is the accepted cost, and 2030-50 residential lands INSIDE the waiver-corrected price band (the old baseline was registered 19-36% low there; industrial likely overshoots its band). WA is the one hydro-dominant state with NO pin: guaranteed hydro displaces its must-take wind (tested -41%), so it runs the HOC-55 compromise instead. Campaign evidence: ~32 BAU probe runs 2026-08-24, docs/findings/bau-fossil-dispatch-cliffs-2026-08-24.md. |  | Indiana | IN
Expected impact: | At 0.90 with the current -2.8% demand anchor: national coal rises from ~531 to a >=657 TWh floor (-10% vs 923ER instead of -27%); displaced generation comes mostly out of gas (~+3.4% -> ~-4%). After the November SEDS 2025 demand re-anchor restores ~119 TWh of demand, least-cost refills gas toward actuals. |  | Iowa | IA
CAVEAT - policy runs: | BGDPbES applies in ALL scenarios, not just BAU. A coal floor mutes price-driven coal redispatch (e.g. carbon tax) until capacity actually retires: policy can still retire coal (guaranteed MWh fall with capacity) but cannot dispatch surviving coal below the floor. Same trade-off already accepted for nuclear (1.0), hydro (0.9), peakers (1.0) and documented for HYECFCA. Staff decision on the fraction (0 restores pure least-cost). |  | Kansas | KS
Caveats - data: | Floor quality inherits HYECFCA/SYSHECF quality: 2025 observed coal CFs include 2025-specific outages and the thin-demand year. States where coal is already economic in EPS (MO, KY, WY: coal beats gas on fuel cost) are unaffected in practice -- least-cost already dispatches above the floor there. Verify against primary sources (EIA-923/860, EPA 7.17/7.20) before adopting; draft for staff review. |  | Kentucky | KY
Rebuild: | python outputs/BGDPbES/_build_bgdpbes_workbook.py |  | Louisiana | LA
|  |  | Maine | ME
|  |  | Maryland | MD
|  |  | Massachusetts | MA
|  |  | Michigan | MI
|  |  | Minnesota | MN
|  |  | Mississippi | MS
|  |  | Missouri | MO
|  |  | Montana | MT
|  |  | Nebraska | NE
|  |  | Nevada | NV
|  |  | New Hampshire | NH
|  |  | New Jersey | NJ
|  |  | New Mexico | NM
|  |  | New York | NY
|  |  | North Carolina | NC
|  |  | North Dakota | ND
|  |  | Ohio | OH
|  |  | Oklahoma | OK
|  |  | Oregon | OR
|  |  | Pennsylvania | PA
|  |  | Rhode Island | RI
|  |  | South Carolina | SC
|  |  | South Dakota | SD
|  |  | Tennessee | TN
|  |  | Texas | TX
|  |  | Utah | UT
|  |  | Vermont | VT
|  |  | Virginia | VA
|  |  | Washington | WA
|  |  | West Virginia | WV
|  |  | Wisconsin | WI
|  |  | Wyoming | WY

## Keys
category | key | value | description | ramp_year | hydro_ramp_value | pin_key (state¦tech) | pin_value
gate | hydro_ramp_state | VT | State whose hydro guarantee is YEAR-VARYING (calibrated 2026-08-11): VT hydro dispatch collapses post-2025 in BAU and ClimateAmbition (must-take builds saturate the requirement; wholesale ~$0-9/MWh by 2030, so no HOC can carry it). The ramp in the year block to the right floors hydro from 2026 on while leaving the calibrated 2025 start year untouched -- a flat guarantee was tested and reorders 2025 dispatch (g=0.7 pushed wind -22% vs observed: guaranteed dispatch runs ahead of the RPS pass). Evidence: docs/findings/vt-hydro-guarantee-ramp-2026-08-11.md. | 2021 | 0 | AL¦hydro | 1
gate | hydro_guarantee_cap | 0.9 | Standing MAX on BGDPbES[hydro] (Olivia, 2026-08-13): no state reaches 1.0, because near-must-run hydro is removed from marginal price formation and accurate prices rank above accurate hydro. Applied as MIN(value, this cap) in the Output hydro row. Bound ID only (was 1.0 -> 0.90, PAIRED with HOC 80 -> 35 because the 1.0 was load-bearing: removing it alone moved ID hydro +1.94% -> -7.18% vs EIA-923 2025). SD stays 0.75 (already under the cap, Tuned-tab row). NOTE the guarantee denominator is state hydro POTENTIAL, not the EIA benchmark, so a ratio test cannot prove a guarantee non-binding -- run it. Evidence: docs/findings/start-year-dispatch-calibration-2026-08-13.md | 2022 | 0 | AR¦hydro | 1
gate | pin_year | 2025 | The single year the I:J pin table applies to (the calibration start year). Coal/gas pins: WA policy-scenario hydro/gas fix + the option-B coal/gas retune (Olivia decisions 2026-08-17); 2025 dispatch response is identical to a flat floor, and pins avoid the measured late-year price costs (WY flat ~29%, MN flat ~21% industry 2050). HYDRO pins added 2026-08-24 (Olivia: guarantee hydro in the start year, calibrate HOC on 2026-29): 13 crowd-out states pinned at target/expected (1.0 everywhere except SD 0.9917 and OR 0.9707), paired with HOC 62 (NV 45, no pin needed). Hydro pins are UNCAPPED in the pin year by the same direction; the 0.90 cap governs all other years. Evidence: qc/bgd_tune_results_optionb*_2026-08-17.csv, docs/findings/wa-2025-guarantee-pin-2026-08-17.md, and docs/findings/bau-fossil-dispatch-cliffs-2026-08-24.md. | 2023 | 0 | AZ¦hydro | 1
|  |  |  | 2024 | 0 | CA¦hydro | 1
|  |  |  | 2025 | 0 | CO¦hydro | 1
|  |  |  | 2026 | 0.3 | GA¦hydro | 1
|  |  |  | 2027 | 0.5 | KY¦hydro | 1
|  |  |  | 2028 | 0.7 | LA¦solar PV | 1
|  |  |  | 2029 | 0.85 | MA¦solar PV | 1
|  |  |  | 2030 | 0.9 | MN¦hydro | 1
|  |  |  | 2031 | 0.9 | MT¦onshore wind | 1
|  |  |  | 2032 | 0.9 | NC¦hydro | 1
|  |  |  | 2033 | 0.9 | NV¦solar PV | 1
|  |  |  | 2034 | 0.9 | OK¦hydro | 1
|  |  |  | 2035 | 0.9 | OK¦onshore wind | 1
|  |  |  | 2036 | 0.9 | OR¦hydro | 1
|  |  |  | 2037 | 0.9 | SD¦hydro | 1
|  |  |  | 2038 | 0.9 | VT¦solar PV | 1
|  |  |  | 2039 | 0.9 | WI¦hydro | 1
|  |  |  | 2040 | 0.9 | WV¦onshore wind | 1
|  |  |  | 2041 | 0.9
|  |  |  | 2042 | 0.9
|  |  |  | 2043 | 0.9
|  |  |  | 2044 | 0.9
|  |  |  | 2045 | 0.9
|  |  |  | 2046 | 0.9
|  |  |  | 2047 | 0.9
|  |  |  | 2048 | 0.9
|  |  |  | 2049 | 0.9
|  |  |  | 2050 | 0.9

## Defaults
tech | default_value | note
hard coal | 0 | Coal/gas guarantees are 2025-only calibration (Olivia 2026-08-17): all years except 2025 are structurally 0, and an untuned/unpinned state has no 2025 floor either. Per-state 2025 values on Tuned/pins.
natural gas steam turbine | 0 | Same 2025-only rule as hard coal; per-state 2025 values on the Tuned tab.
natural gas combined cycle | 0 | Same 2025-only rule as hard coal; per-state 2025 values on the Tuned tab and the pin table.
nuclear | 1 | Structural must-run convention inherited from eps-us.
hydro | 0.9 | Long-standing 0.90 convention, enforced as a MAX by the Keys hydro_guarantee_cap (Olivia 2026-08-13). Exceptions: SD 0.75 and WA 0.0 on the Tuned tab; VT year-varying ramp in the Keys F:G block; 12 crowd-out states carry an UNCAPPED 2025-only pin (Keys I:J, 2026-08-24) so the start year matches EIA-923 while HOC governs 2026+.
onshore wind | 0 | VRE dispatches through the RPS/least-cost passes; no guarantee.
solar PV | 0 | VRE dispatches through the RPS/least-cost passes; no guarantee.
solar thermal | 0 | VRE dispatches through the RPS/least-cost passes; no guarantee.
biomass | 1 | Must-run convention inherited from eps-us.
geothermal | 1 | Must-run convention inherited from eps-us.
petroleum | 1 | Fallback only: every state carries a computed per-state value on the Tuned tab, applied in ALL years (the documented exception to the 2025-only rule, Olivia 2026-08-26). The old eps-us must-run 1.0 would dispatch oil at natural-gas-peaker rates now that SYSHECF mirrors the peaker (+105% vs EIA-923 2025 nationally).
natural gas peaker | 1 | Structural convention alongside nuclear/hydro, not calibration. Exceptions (MT/ND/VA/WA/WV) on the Tuned tab; ND also has a 2025 pin.
lignite | 0 | Same 2025-only rule as hard coal; per-state 2025 values on Tuned.
offshore wind | 0 | VRE dispatches through the RPS/least-cost passes; no guarantee.
crude oil | 1 | Must-run convention inherited from eps-us.
heavy or residual fuel oil | 0 | Inherited from eps-us.
municipal solid waste | 0 | Inherited from eps-us.
hard coal w CCS | 0 | ZEROED 2026-08-21 (Olivia): fleet does not exist in the 2025 start year; previous value (0.15) was the eps-us national template, not a state calibration. Zero lets least-cost dispatch decide if this tech is ever built in a policy scenario instead of forcing near-must-run operation.
natural gas combined cycle w CCS | 0 | ZEROED 2026-08-21 (Olivia): fleet does not exist in the 2025 start year; previous value (0.15) was the eps-us national template, not a state calibration. Zero lets least-cost dispatch decide if this tech is ever built in a policy scenario instead of forcing near-must-run operation.
biomass w CCS | 0 | ZEROED 2026-08-21 (Olivia): fleet does not exist in the 2025 start year; previous value (1) was the eps-us national template, not a state calibration. Zero lets least-cost dispatch decide if this tech is ever built in a policy scenario instead of forcing near-must-run operation.
lignite w CCS | 0 | ZEROED 2026-08-21 (Olivia): fleet does not exist in the 2025 start year; previous value (1) was the eps-us national template, not a state calibration. Zero lets least-cost dispatch decide if this tech is ever built in a policy scenario instead of forcing near-must-run operation.
small modular reactor | 0 | ZEROED 2026-08-21 (Olivia): fleet does not exist in the 2025 start year; previous value (0) was the eps-us national template, not a state calibration. Zero lets least-cost dispatch decide if this tech is ever built in a policy scenario instead of forcing near-must-run operation.
hydrogen combustion turbine | 1 | Inherited from eps-us; deliberately KEPT at 1.0 when the six w-CCS/SMR/H2-CC rows were zeroed 2026-08-21.
hydrogen combined cycle | 0 | ZEROED 2026-08-21 (Olivia): fleet does not exist in the 2025 start year; previous value (1) was the eps-us national template, not a state calibration. Zero lets least-cost dispatch decide if this tech is ever built in a policy scenario instead of forcing near-must-run operation.

## Tuned
state | tech | tuned_value | key (state¦tech) | note
AL | natural gas combined cycle | 0.3062 | AL¦natural gas combined cycle | 2026-09-02 cross-state dispatch retune rounds 7-8 (same directive and method as the round-1-6 states): NGCC floor 0.148665 -> 0.3062 closes the last tunable opposite-sign split -- coal -0.7% / gas -1.3% / hydro and solar 0.0%. Round CSVs: qc/calibration/dispatch_retune_0902_round{7,8}.csv.
AL | petroleum | 0.4912 | AL¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 7.5 GWh / (cap 42.6 MW x CF 0.0411 x 8760) = 0.4912
AR | natural gas combined cycle | 0.7 | AR¦natural gas combined cycle | 2026-08-31 post-MCF retune (docs/findings/dispatch-recalibration-post-mcf-2026-08-31.md): floors re-solved from zero after the firm-credit MCF derate (0.9 thermal / 0.95 NGCC) invalidated the 08-28 values. One lever per state (NGCC or hard coal), balance-point target, secant; AR/FL/MS hand-interpolated on coal_err=gas_err (0.7/0.5/0.854). Source: qc/calibration/bgdpbes_0831_round3.csv + the finding doc final-floor table. RESTORED 2026-09-01 after the 08:36 InputData sync wiped the run trees (docs/findings/bau-0901-floor-revert-2026-09-01.md); VT excluded throughout (bad distributed-solar inputs).
AR | petroleum | 1 | AR¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 43.9 GWh / (cap 9.0 MW x CF 0.1014 x 8760) = 5.4865 -- CLIPPED at 1.0; 43.9 GWh of this burns at units whose capacity BHRaSYC books under another row, so it is unreachable
AZ | hard coal | 0.64913 | AZ¦hard coal | 2026-08-31 post-MCF retune (docs/findings/dispatch-recalibration-post-mcf-2026-08-31.md): floors re-solved from zero after the firm-credit MCF derate (0.9 thermal / 0.95 NGCC) invalidated the 08-28 values. One lever per state (NGCC or hard coal), balance-point target, secant; AR/FL/MS hand-interpolated on coal_err=gas_err (0.7/0.5/0.854). Source: qc/calibration/bgdpbes_0831_round3.csv + the finding doc final-floor table. RESTORED 2026-09-01 after the 08:36 InputData sync wiped the run trees (docs/findings/bau-0901-floor-revert-2026-09-01.md); VT excluded throughout (bad distributed-solar inputs).
AZ | petroleum | 0.625 | AZ¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 40.8 GWh / (cap 84.7 MW x CF 0.0880 x 8760) = 0.6250
CA | petroleum | 0.3235 | CA¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 31.1 GWh / (cap 224.0 MW x CF 0.0491 x 8760) = 0.3235
CO | natural gas combined cycle | 0.92054 | CO¦natural gas combined cycle | 2026-08-31 post-MCF retune (docs/findings/dispatch-recalibration-post-mcf-2026-08-31.md): floors re-solved from zero after the firm-credit MCF derate (0.9 thermal / 0.95 NGCC) invalidated the 08-28 values. One lever per state (NGCC or hard coal), balance-point target, secant; AR/FL/MS hand-interpolated on coal_err=gas_err (0.7/0.5/0.854). Source: qc/calibration/bgdpbes_0831_round3.csv + the finding doc final-floor table. RESTORED 2026-09-01 after the 08:36 InputData sync wiped the run trees (docs/findings/bau-0901-floor-revert-2026-09-01.md); VT excluded throughout (bad distributed-solar inputs).
CO | petroleum | 0.087 | CO¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 13.5 GWh / (cap 148.1 MW x CF 0.1198 x 8760) = 0.0870
CT | natural gas combined cycle | 0.96805 | CT¦natural gas combined cycle | 2026-08-31 post-MCF retune (docs/findings/dispatch-recalibration-post-mcf-2026-08-31.md): floors re-solved from zero after the firm-credit MCF derate (0.9 thermal / 0.95 NGCC) invalidated the 08-28 values. One lever per state (NGCC or hard coal), balance-point target, secant; AR/FL/MS hand-interpolated on coal_err=gas_err (0.7/0.5/0.854). Source: qc/calibration/bgdpbes_0831_round3.csv + the finding doc final-floor table. RESTORED 2026-09-01 after the 08:36 InputData sync wiped the run trees (docs/findings/bau-0901-floor-revert-2026-09-01.md); VT excluded throughout (bad distributed-solar inputs).
CT | petroleum | 0.3608 | CT¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 240.2 GWh / (cap 2197.2 MW x CF 0.0346 x 8760) = 0.3608
DE | petroleum | 1 | DE¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 71.4 GWh / (cap 111.1 MW x CF 0.0608 x 8760) = 1.2064 -- CLIPPED at 1.0; 74.0 GWh of this burns at units whose capacity BHRaSYC books under another row, so it is unreachable
FL | natural gas combined cycle | 0.617 | FL¦natural gas combined cycle | 2026-09-01 touch-up round on the noon bau-0901 basis (docs/findings/bgdpbes-touchup-2026-09-01.md): SD/OH coal and FL/WI NGCC floors re-solved by two-point secant from the 08-31 values (FL hand-interpolated on coal_err=gas_err, the 0831-doc blind-spot case); WA re-enters the calibration with the Centralia BCRbQ retirement moved to the 2026 column (RUN-TREE edit, upstream fix owed under O68) and HOC 55, coal floor solved in the floored regime. WA floor is only meaningful with the BCRbQ fix deployed alongside. All other states carried forward from bgd_tune_results_2026-08-31.csv unchanged; VT excluded throughout.
FL | petroleum | 1 | FL¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 1217.9 GWh / (cap 1594.9 MW x CF 0.0762 x 8760) = 1.1435 -- CLIPPED at 1.0; 1170.2 GWh of this burns at units whose capacity BHRaSYC books under another row, so it is unreachable
GA | natural gas combined cycle | 0.036446 | GA¦natural gas combined cycle | 2026-08-31 post-MCF retune (docs/findings/dispatch-recalibration-post-mcf-2026-08-31.md): floors re-solved from zero after the firm-credit MCF derate (0.9 thermal / 0.95 NGCC) invalidated the 08-28 values. One lever per state (NGCC or hard coal), balance-point target, secant; AR/FL/MS hand-interpolated on coal_err=gas_err (0.7/0.5/0.854). Source: qc/calibration/bgdpbes_0831_round3.csv + the finding doc final-floor table. RESTORED 2026-09-01 after the 08:36 InputData sync wiped the run trees (docs/findings/bau-0901-floor-revert-2026-09-01.md); VT excluded throughout (bad distributed-solar inputs).
GA | petroleum | 0.3348 | GA¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 160.4 GWh / (cap 1014.3 MW x CF 0.0539 x 8760) = 0.3348
IA | natural gas combined cycle | 0.255 | IA¦natural gas combined cycle | 2026-09-02 cross-state dispatch retune, rounds 1-6 on the bau-0902 basis (Olivia's alignment directive: no opposite-sign coal/gas splits; hydro/wind/solar within 1-2% unless a very small share; both-low/both-high accepted where total generation is short/over). Levers: NGCC/NGST/hard-coal/peaker 2025 guarantee floors read from the run tree after round 6; TN/WY/MT hydro via HYECFCA (hyecfca_retune_2026-09-02.csv). MT: peaker guarantee 1.0 -> 0 (per-state exception to the uniform must-run peaker, K14) and hard-coal floor removed (coal economic). LA: NGST 0.5 is a TRADEOFF -- coal +19.6% -> +8.0% but solar -7.4% -> -16.2% (crowding); revert to 0 to trade back. Round CSVs: qc/calibration/dispatch_retune_0902_round{1..6}.csv. All other states carried forward unchanged.
IA | petroleum | 0.2324 | IA¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 65.2 GWh / (cap 775.9 MW x CF 0.0412 x 8760) = 0.2324
ID | natural gas combined cycle | 0.52936 | ID¦natural gas combined cycle | 2026-08-31 post-MCF retune (docs/findings/dispatch-recalibration-post-mcf-2026-08-31.md): floors re-solved from zero after the firm-credit MCF derate (0.9 thermal / 0.95 NGCC) invalidated the 08-28 values. One lever per state (NGCC or hard coal), balance-point target, secant; AR/FL/MS hand-interpolated on coal_err=gas_err (0.7/0.5/0.854). Source: qc/calibration/bgdpbes_0831_round3.csv + the finding doc final-floor table. RESTORED 2026-09-01 after the 08:36 InputData sync wiped the run trees (docs/findings/bau-0901-floor-revert-2026-09-01.md); VT excluded throughout (bad distributed-solar inputs).
ID | petroleum | 0.0013 | ID¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 0.0 GWh / (cap 5.6 MW x CF 0.5619 x 8760) = 0.0013
IL | natural gas combined cycle | 0.421 | IL¦natural gas combined cycle | 2026-09-02 cross-state dispatch retune, rounds 1-6 on the bau-0902 basis (Olivia's alignment directive: no opposite-sign coal/gas splits; hydro/wind/solar within 1-2% unless a very small share; both-low/both-high accepted where total generation is short/over). Levers: NGCC/NGST/hard-coal/peaker 2025 guarantee floors read from the run tree after round 6; TN/WY/MT hydro via HYECFCA (hyecfca_retune_2026-09-02.csv). MT: peaker guarantee 1.0 -> 0 (per-state exception to the uniform must-run peaker, K14) and hard-coal floor removed (coal economic). LA: NGST 0.5 is a TRADEOFF -- coal +19.6% -> +8.0% but solar -7.4% -> -16.2% (crowding); revert to 0 to trade back. Round CSVs: qc/calibration/dispatch_retune_0902_round{1..6}.csv. All other states carried forward unchanged.
IL | petroleum | 0.1582 | IL¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 34.2 GWh / (cap 650.0 MW x CF 0.0379 x 8760) = 0.1582
IN | natural gas combined cycle | 0.81539 | IN¦natural gas combined cycle | 2026-08-31 post-MCF retune (docs/findings/dispatch-recalibration-post-mcf-2026-08-31.md): floors re-solved from zero after the firm-credit MCF derate (0.9 thermal / 0.95 NGCC) invalidated the 08-28 values. One lever per state (NGCC or hard coal), balance-point target, secant; AR/FL/MS hand-interpolated on coal_err=gas_err (0.7/0.5/0.854). Source: qc/calibration/bgdpbes_0831_round3.csv + the finding doc final-floor table. RESTORED 2026-09-01 after the 08:36 InputData sync wiped the run trees (docs/findings/bau-0901-floor-revert-2026-09-01.md); VT excluded throughout (bad distributed-solar inputs).
IN | petroleum | 1 | IN¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 129.4 GWh / (cap 62.8 MW x CF 0.1416 x 8760) = 1.6617 -- CLIPPED at 1.0; 127.8 GWh of this burns at units whose capacity BHRaSYC books under another row, so it is unreachable
KS | natural gas combined cycle | 0.69385 | KS¦natural gas combined cycle | 2026-08-31 post-MCF retune (docs/findings/dispatch-recalibration-post-mcf-2026-08-31.md): floors re-solved from zero after the firm-credit MCF derate (0.9 thermal / 0.95 NGCC) invalidated the 08-28 values. One lever per state (NGCC or hard coal), balance-point target, secant; AR/FL/MS hand-interpolated on coal_err=gas_err (0.7/0.5/0.854). Source: qc/calibration/bgdpbes_0831_round3.csv + the finding doc final-floor table. RESTORED 2026-09-01 after the 08:36 InputData sync wiped the run trees (docs/findings/bau-0901-floor-revert-2026-09-01.md); VT excluded throughout (bad distributed-solar inputs).
KS | petroleum | 0.1661 | KS¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 74.9 GWh / (cap 540.1 MW x CF 0.0952 x 8760) = 0.1661
KY | hard coal | 0.084824 | KY¦hard coal | 2026-08-31 post-MCF retune (docs/findings/dispatch-recalibration-post-mcf-2026-08-31.md): floors re-solved from zero after the firm-credit MCF derate (0.9 thermal / 0.95 NGCC) invalidated the 08-28 values. One lever per state (NGCC or hard coal), balance-point target, secant; AR/FL/MS hand-interpolated on coal_err=gas_err (0.7/0.5/0.854). Source: qc/calibration/bgdpbes_0831_round3.csv + the finding doc final-floor table. RESTORED 2026-09-01 after the 08:36 InputData sync wiped the run trees (docs/findings/bau-0901-floor-revert-2026-09-01.md); VT excluded throughout (bad distributed-solar inputs).
KY | petroleum | 1 | KY¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 76.8 GWh / (cap 10.8 MW x CF 0.0985 x 8760) = 8.2489 -- CLIPPED at 1.0; 76.5 GWh of this burns at units whose capacity BHRaSYC books under another row, so it is unreachable
LA | natural gas steam turbine | 0.5 | LA¦natural gas steam turbine | 2026-09-02 cross-state dispatch retune, rounds 1-6 on the bau-0902 basis (Olivia's alignment directive: no opposite-sign coal/gas splits; hydro/wind/solar within 1-2% unless a very small share; both-low/both-high accepted where total generation is short/over). Levers: NGCC/NGST/hard-coal/peaker 2025 guarantee floors read from the run tree after round 6; TN/WY/MT hydro via HYECFCA (hyecfca_retune_2026-09-02.csv). MT: peaker guarantee 1.0 -> 0 (per-state exception to the uniform must-run peaker, K14) and hard-coal floor removed (coal economic). LA: NGST 0.5 is a TRADEOFF -- coal +19.6% -> +8.0% but solar -7.4% -> -16.2% (crowding); revert to 0 to trade back. Round CSVs: qc/calibration/dispatch_retune_0902_round{1..6}.csv. All other states carried forward unchanged. UPDATE rounds 9-10: solar un-eaten per Olivia -- solar PV guarantee 1.0 (builder VRE_FALLBACK_2025) + LA solar HYECFCA anchor trim lands solar 0.0% with coal +7.8 / gas -1.8; the NGST-0.5 tradeoff note above is superseded.
LA | natural gas combined cycle | 0.91886 | LA¦natural gas combined cycle | 2026-09-02 cross-state dispatch retune, rounds 1-6 on the bau-0902 basis (Olivia's alignment directive: no opposite-sign coal/gas splits; hydro/wind/solar within 1-2% unless a very small share; both-low/both-high accepted where total generation is short/over). Levers: NGCC/NGST/hard-coal/peaker 2025 guarantee floors read from the run tree after round 6; TN/WY/MT hydro via HYECFCA (hyecfca_retune_2026-09-02.csv). MT: peaker guarantee 1.0 -> 0 (per-state exception to the uniform must-run peaker, K14) and hard-coal floor removed (coal economic). LA: NGST 0.5 is a TRADEOFF -- coal +19.6% -> +8.0% but solar -7.4% -> -16.2% (crowding); revert to 0 to trade back. Round CSVs: qc/calibration/dispatch_retune_0902_round{1..6}.csv. All other states carried forward unchanged. UPDATE rounds 9-10: solar un-eaten per Olivia -- solar PV guarantee 1.0 (builder VRE_FALLBACK_2025) + LA solar HYECFCA anchor trim lands solar 0.0% with coal +7.8 / gas -1.8; the NGST-0.5 tradeoff note above is superseded.
LA | petroleum | 0.8543 | LA¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 450.8 GWh / (cap 839.0 MW x CF 0.0718 x 8760) = 0.8543
MA | natural gas combined cycle | 1 | MA¦natural gas combined cycle | 2026-08-31 post-MCF retune (docs/findings/dispatch-recalibration-post-mcf-2026-08-31.md): floors re-solved from zero after the firm-credit MCF derate (0.9 thermal / 0.95 NGCC) invalidated the 08-28 values. One lever per state (NGCC or hard coal), balance-point target, secant; AR/FL/MS hand-interpolated on coal_err=gas_err (0.7/0.5/0.854). Source: qc/calibration/bgdpbes_0831_round3.csv + the finding doc final-floor table. RESTORED 2026-09-01 after the 08:36 InputData sync wiped the run trees (docs/findings/bau-0901-floor-revert-2026-09-01.md); VT excluded throughout (bad distributed-solar inputs).
MA | petroleum | 0.1877 | MA¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 400.6 GWh / (cap 2180.7 MW x CF 0.1117 x 8760) = 0.1877
MD | hard coal | 0.10321 | MD¦hard coal | 2026-08-31 post-MCF retune (docs/findings/dispatch-recalibration-post-mcf-2026-08-31.md): floors re-solved from zero after the firm-credit MCF derate (0.9 thermal / 0.95 NGCC) invalidated the 08-28 values. One lever per state (NGCC or hard coal), balance-point target, secant; AR/FL/MS hand-interpolated on coal_err=gas_err (0.7/0.5/0.854). Source: qc/calibration/bgdpbes_0831_round3.csv + the finding doc final-floor table. RESTORED 2026-09-01 after the 08:36 InputData sync wiped the run trees (docs/findings/bau-0901-floor-revert-2026-09-01.md); VT excluded throughout (bad distributed-solar inputs).
MD | petroleum | 0.5588 | MD¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 378.9 GWh / (cap 1537.4 MW x CF 0.0503 x 8760) = 0.5588
ME | petroleum | 1 | ME¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 148.0 GWh / (cap 842.9 MW x CF 0.0079 x 8760) = 2.5301 -- CLIPPED at 1.0; 8.6 GWh of this burns at units whose capacity BHRaSYC books under another row, so it is unreachable
MI | hard coal | 0.4866 | MI¦hard coal | 2026-08-31 post-MCF retune (docs/findings/dispatch-recalibration-post-mcf-2026-08-31.md): floors re-solved from zero after the firm-credit MCF derate (0.9 thermal / 0.95 NGCC) invalidated the 08-28 values. One lever per state (NGCC or hard coal), balance-point target, secant; AR/FL/MS hand-interpolated on coal_err=gas_err (0.7/0.5/0.854). Source: qc/calibration/bgdpbes_0831_round3.csv + the finding doc final-floor table. RESTORED 2026-09-01 after the 08:36 InputData sync wiped the run trees (docs/findings/bau-0901-floor-revert-2026-09-01.md); VT excluded throughout (bad distributed-solar inputs).
MI | petroleum | 1 | MI¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 1582.2 GWh / (cap 373.9 MW x CF 0.2641 x 8760) = 1.8294 -- CLIPPED at 1.0; 1572.8 GWh of this burns at units whose capacity BHRaSYC books under another row, so it is unreachable
MN | natural gas combined cycle | 0.07431 | MN¦natural gas combined cycle | 2026-08-31 post-MCF retune (docs/findings/dispatch-recalibration-post-mcf-2026-08-31.md): floors re-solved from zero after the firm-credit MCF derate (0.9 thermal / 0.95 NGCC) invalidated the 08-28 values. One lever per state (NGCC or hard coal), balance-point target, secant; AR/FL/MS hand-interpolated on coal_err=gas_err (0.7/0.5/0.854). Source: qc/calibration/bgdpbes_0831_round3.csv + the finding doc final-floor table. RESTORED 2026-09-01 after the 08:36 InputData sync wiped the run trees (docs/findings/bau-0901-floor-revert-2026-09-01.md); VT excluded throughout (bad distributed-solar inputs).
MN | petroleum | 0.0277 | MN¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 18.2 GWh / (cap 727.3 MW x CF 0.1033 x 8760) = 0.0277
MO | hard coal | 0.15 | MO¦hard coal | 2026-09-02 cross-state dispatch retune, rounds 1-6 on the bau-0902 basis (Olivia's alignment directive: no opposite-sign coal/gas splits; hydro/wind/solar within 1-2% unless a very small share; both-low/both-high accepted where total generation is short/over). Levers: NGCC/NGST/hard-coal/peaker 2025 guarantee floors read from the run tree after round 6; TN/WY/MT hydro via HYECFCA (hyecfca_retune_2026-09-02.csv). MT: peaker guarantee 1.0 -> 0 (per-state exception to the uniform must-run peaker, K14) and hard-coal floor removed (coal economic). LA: NGST 0.5 is a TRADEOFF -- coal +19.6% -> +8.0% but solar -7.4% -> -16.2% (crowding); revert to 0 to trade back. Round CSVs: qc/calibration/dispatch_retune_0902_round{1..6}.csv. All other states carried forward unchanged.
MO | natural gas combined cycle | 0.923 | MO¦natural gas combined cycle | 2026-09-02 cross-state dispatch retune, rounds 1-6 on the bau-0902 basis (Olivia's alignment directive: no opposite-sign coal/gas splits; hydro/wind/solar within 1-2% unless a very small share; both-low/both-high accepted where total generation is short/over). Levers: NGCC/NGST/hard-coal/peaker 2025 guarantee floors read from the run tree after round 6; TN/WY/MT hydro via HYECFCA (hyecfca_retune_2026-09-02.csv). MT: peaker guarantee 1.0 -> 0 (per-state exception to the uniform must-run peaker, K14) and hard-coal floor removed (coal economic). LA: NGST 0.5 is a TRADEOFF -- coal +19.6% -> +8.0% but solar -7.4% -> -16.2% (crowding); revert to 0 to trade back. Round CSVs: qc/calibration/dispatch_retune_0902_round{1..6}.csv. All other states carried forward unchanged.
MO | petroleum | 0.2088 | MO¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 133.4 GWh / (cap 1038.2 MW x CF 0.0702 x 8760) = 0.2088
MS | natural gas combined cycle | 0.854 | MS¦natural gas combined cycle | 2026-08-31 post-MCF retune (docs/findings/dispatch-recalibration-post-mcf-2026-08-31.md): floors re-solved from zero after the firm-credit MCF derate (0.9 thermal / 0.95 NGCC) invalidated the 08-28 values. One lever per state (NGCC or hard coal), balance-point target, secant; AR/FL/MS hand-interpolated on coal_err=gas_err (0.7/0.5/0.854). Source: qc/calibration/bgdpbes_0831_round3.csv + the finding doc final-floor table. RESTORED 2026-09-01 after the 08:36 InputData sync wiped the run trees (docs/findings/bau-0901-floor-revert-2026-09-01.md); VT excluded throughout (bad distributed-solar inputs).
MS | petroleum | 0.3834 | MS¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 5.5 GWh / (cap 9.0 MW x CF 0.1833 x 8760) = 0.3834
MT | petroleum | 1 | MT¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 468.0 GWh / (cap 52.0 MW x CF 0.2377 x 8760) = 4.3229 -- CLIPPED at 1.0; 12.6 GWh of this burns at units whose capacity BHRaSYC books under another row, so it is unreachable
MT | natural gas peaker | 0 | MT¦natural gas peaker | 2026-09-02 cross-state dispatch retune, rounds 1-6 on the bau-0902 basis (Olivia's alignment directive: no opposite-sign coal/gas splits; hydro/wind/solar within 1-2% unless a very small share; both-low/both-high accepted where total generation is short/over). Levers: NGCC/NGST/hard-coal/peaker 2025 guarantee floors read from the run tree after round 6; TN/WY/MT hydro via HYECFCA (hyecfca_retune_2026-09-02.csv). MT: peaker guarantee 1.0 -> 0 (per-state exception to the uniform must-run peaker, K14) and hard-coal floor removed (coal economic). LA: NGST 0.5 is a TRADEOFF -- coal +19.6% -> +8.0% but solar -7.4% -> -16.2% (crowding); revert to 0 to trade back. Round CSVs: qc/calibration/dispatch_retune_0902_round{1..6}.csv. All other states carried forward unchanged.
NC | hard coal | 0.41271 | NC¦hard coal | 2026-08-31 post-MCF retune (docs/findings/dispatch-recalibration-post-mcf-2026-08-31.md): floors re-solved from zero after the firm-credit MCF derate (0.9 thermal / 0.95 NGCC) invalidated the 08-28 values. One lever per state (NGCC or hard coal), balance-point target, secant; AR/FL/MS hand-interpolated on coal_err=gas_err (0.7/0.5/0.854). Source: qc/calibration/bgdpbes_0831_round3.csv + the finding doc final-floor table. RESTORED 2026-09-01 after the 08:36 InputData sync wiped the run trees (docs/findings/bau-0901-floor-revert-2026-09-01.md); VT excluded throughout (bad distributed-solar inputs).
NC | petroleum | 0.5501 | NC¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 226.2 GWh / (cap 425.7 MW x CF 0.1103 x 8760) = 0.5501
ND | hard coal | 1 | ND¦hard coal | 2026-09-02 retune rounds 9-11: ND coal is mostly LIGNITE (the 0831 tool levers hard coal only, which was already at 1.0) -- lignite floor 0 -> 0.384 plus peaker guarantee 1.0 -> 0.8 (2025-only, MT-style exception) take ND from coal -3.1 / gas +19.6 to coal +0.1 / gas -0.4 / wind -0.9. Rounds: dispatch_retune_0902_round{9,10,11}.csv.
ND | petroleum | 0.1529 | ND¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 31.4 GWh / (cap 54.6 MW x CF 0.4289 x 8760) = 0.1529
ND | natural gas peaker | 0.8 | ND¦natural gas peaker | 2026-09-02 retune rounds 9-11: ND coal is mostly LIGNITE (the 0831 tool levers hard coal only, which was already at 1.0) -- lignite floor 0 -> 0.384 plus peaker guarantee 1.0 -> 0.8 (2025-only, MT-style exception) take ND from coal -3.1 / gas +19.6 to coal +0.1 / gas -0.4 / wind -0.9. Rounds: dispatch_retune_0902_round{9,10,11}.csv.
ND | lignite | 0.384 | ND¦lignite | 2026-09-02 retune rounds 9-11: ND coal is mostly LIGNITE (the 0831 tool levers hard coal only, which was already at 1.0) -- lignite floor 0 -> 0.384 plus peaker guarantee 1.0 -> 0.8 (2025-only, MT-style exception) take ND from coal -3.1 / gas +19.6 to coal +0.1 / gas -0.4 / wind -0.9. Rounds: dispatch_retune_0902_round{9,10,11}.csv.
NE | natural gas combined cycle | 1 | NE¦natural gas combined cycle | 2026-08-31 post-MCF retune (docs/findings/dispatch-recalibration-post-mcf-2026-08-31.md): floors re-solved from zero after the firm-credit MCF derate (0.9 thermal / 0.95 NGCC) invalidated the 08-28 values. One lever per state (NGCC or hard coal), balance-point target, secant; AR/FL/MS hand-interpolated on coal_err=gas_err (0.7/0.5/0.854). Source: qc/calibration/bgdpbes_0831_round3.csv + the finding doc final-floor table. RESTORED 2026-09-01 after the 08:36 InputData sync wiped the run trees (docs/findings/bau-0901-floor-revert-2026-09-01.md); VT excluded throughout (bad distributed-solar inputs).
NE | petroleum | 0.3078 | NE¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 64.1 GWh / (cap 373.7 MW x CF 0.0637 x 8760) = 0.3078
NH | natural gas combined cycle | 0.76283 | NH¦natural gas combined cycle | 2026-08-31 post-MCF retune (docs/findings/dispatch-recalibration-post-mcf-2026-08-31.md): floors re-solved from zero after the firm-credit MCF derate (0.9 thermal / 0.95 NGCC) invalidated the 08-28 values. One lever per state (NGCC or hard coal), balance-point target, secant; AR/FL/MS hand-interpolated on coal_err=gas_err (0.7/0.5/0.854). Source: qc/calibration/bgdpbes_0831_round3.csv + the finding doc final-floor table. RESTORED 2026-09-01 after the 08:36 InputData sync wiped the run trees (docs/findings/bau-0901-floor-revert-2026-09-01.md); VT excluded throughout (bad distributed-solar inputs).
NH | petroleum | 1 | NH¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 169.4 GWh / (cap 82.1 MW x CF 0.1096 x 8760) = 2.1489 -- CLIPPED at 1.0; 167.7 GWh of this burns at units whose capacity BHRaSYC books under another row, so it is unreachable
NJ | petroleum | 0.8711 | NJ¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 162.7 GWh / (cap 270.0 MW x CF 0.0790 x 8760) = 0.8711
NM | hard coal | 0.95341 | NM¦hard coal | 2026-08-31 post-MCF retune (docs/findings/dispatch-recalibration-post-mcf-2026-08-31.md): floors re-solved from zero after the firm-credit MCF derate (0.9 thermal / 0.95 NGCC) invalidated the 08-28 values. One lever per state (NGCC or hard coal), balance-point target, secant; AR/FL/MS hand-interpolated on coal_err=gas_err (0.7/0.5/0.854). Source: qc/calibration/bgdpbes_0831_round3.csv + the finding doc final-floor table. RESTORED 2026-09-01 after the 08:36 InputData sync wiped the run trees (docs/findings/bau-0901-floor-revert-2026-09-01.md); VT excluded throughout (bad distributed-solar inputs).
NM | petroleum | 0.0137 | NM¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 0.4 GWh / (cap 17.0 MW x CF 0.2082 x 8760) = 0.0137
NV | hard coal | 0.68186 | NV¦hard coal | 2026-08-31 post-MCF retune (docs/findings/dispatch-recalibration-post-mcf-2026-08-31.md): floors re-solved from zero after the firm-credit MCF derate (0.9 thermal / 0.95 NGCC) invalidated the 08-28 values. One lever per state (NGCC or hard coal), balance-point target, secant; AR/FL/MS hand-interpolated on coal_err=gas_err (0.7/0.5/0.854). Source: qc/calibration/bgdpbes_0831_round3.csv + the finding doc final-floor table. RESTORED 2026-09-01 after the 08:36 InputData sync wiped the run trees (docs/findings/bau-0901-floor-revert-2026-09-01.md); VT excluded throughout (bad distributed-solar inputs).
NV | petroleum | 1 | NV¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 7.3 GWh / (cap 6.0 MW x CF 0.0307 x 8760) = 4.5291 -- CLIPPED at 1.0; 7.3 GWh of this burns at units whose capacity BHRaSYC books under another row, so it is unreachable
NY | natural gas combined cycle | 0.93679 | NY¦natural gas combined cycle | 2026-08-31 post-MCF retune (docs/findings/dispatch-recalibration-post-mcf-2026-08-31.md): floors re-solved from zero after the firm-credit MCF derate (0.9 thermal / 0.95 NGCC) invalidated the 08-28 values. One lever per state (NGCC or hard coal), balance-point target, secant; AR/FL/MS hand-interpolated on coal_err=gas_err (0.7/0.5/0.854). Source: qc/calibration/bgdpbes_0831_round3.csv + the finding doc final-floor table. RESTORED 2026-09-01 after the 08:36 InputData sync wiped the run trees (docs/findings/bau-0901-floor-revert-2026-09-01.md); VT excluded throughout (bad distributed-solar inputs).
NY | petroleum | 0.2318 | NY¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 1195.6 GWh / (cap 3245.0 MW x CF 0.1814 x 8760) = 0.2318
OH | hard coal | 0.48862 | OH¦hard coal | 2026-09-01 touch-up round on the noon bau-0901 basis (docs/findings/bgdpbes-touchup-2026-09-01.md): SD/OH coal and FL/WI NGCC floors re-solved by two-point secant from the 08-31 values (FL hand-interpolated on coal_err=gas_err, the 0831-doc blind-spot case); WA re-enters the calibration with the Centralia BCRbQ retirement moved to the 2026 column (RUN-TREE edit, upstream fix owed under O68) and HOC 55, coal floor solved in the floored regime. WA floor is only meaningful with the BCRbQ fix deployed alongside. All other states carried forward from bgd_tune_results_2026-08-31.csv unchanged; VT excluded throughout.
OH | petroleum | 1 | OH¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 1279.5 GWh / (cap 630.2 MW x CF 0.1728 x 8760) = 1.3414 -- CLIPPED at 1.0; 1263.2 GWh of this burns at units whose capacity BHRaSYC books under another row, so it is unreachable
OK | hard coal | 0.11 | OK¦hard coal | 2026-09-02 cross-state dispatch retune, rounds 1-6 on the bau-0902 basis (Olivia's alignment directive: no opposite-sign coal/gas splits; hydro/wind/solar within 1-2% unless a very small share; both-low/both-high accepted where total generation is short/over). Levers: NGCC/NGST/hard-coal/peaker 2025 guarantee floors read from the run tree after round 6; TN/WY/MT hydro via HYECFCA (hyecfca_retune_2026-09-02.csv). MT: peaker guarantee 1.0 -> 0 (per-state exception to the uniform must-run peaker, K14) and hard-coal floor removed (coal economic). LA: NGST 0.5 is a TRADEOFF -- coal +19.6% -> +8.0% but solar -7.4% -> -16.2% (crowding); revert to 0 to trade back. Round CSVs: qc/calibration/dispatch_retune_0902_round{1..6}.csv. All other states carried forward unchanged.
OK | natural gas combined cycle | 0.85928 | OK¦natural gas combined cycle | 2026-09-02 cross-state dispatch retune, rounds 1-6 on the bau-0902 basis (Olivia's alignment directive: no opposite-sign coal/gas splits; hydro/wind/solar within 1-2% unless a very small share; both-low/both-high accepted where total generation is short/over). Levers: NGCC/NGST/hard-coal/peaker 2025 guarantee floors read from the run tree after round 6; TN/WY/MT hydro via HYECFCA (hyecfca_retune_2026-09-02.csv). MT: peaker guarantee 1.0 -> 0 (per-state exception to the uniform must-run peaker, K14) and hard-coal floor removed (coal economic). LA: NGST 0.5 is a TRADEOFF -- coal +19.6% -> +8.0% but solar -7.4% -> -16.2% (crowding); revert to 0 to trade back. Round CSVs: qc/calibration/dispatch_retune_0902_round{1..6}.csv. All other states carried forward unchanged.
OK | petroleum | 0.9286 | OK¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 33.3 GWh / (cap 35.9 MW x CF 0.1141 x 8760) = 0.9286
OR | natural gas combined cycle | 0.17886 | OR¦natural gas combined cycle | 2026-08-31 post-MCF retune (docs/findings/dispatch-recalibration-post-mcf-2026-08-31.md): floors re-solved from zero after the firm-credit MCF derate (0.9 thermal / 0.95 NGCC) invalidated the 08-28 values. One lever per state (NGCC or hard coal), balance-point target, secant; AR/FL/MS hand-interpolated on coal_err=gas_err (0.7/0.5/0.854). Source: qc/calibration/bgdpbes_0831_round3.csv + the finding doc final-floor table. RESTORED 2026-09-01 after the 08:36 InputData sync wiped the run trees (docs/findings/bau-0901-floor-revert-2026-09-01.md); VT excluded throughout (bad distributed-solar inputs).
OR | petroleum | 0 | OR¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): no start-year petroleum fleet (0 MW): no guarantee
PA | hard coal | 0.23078 | PA¦hard coal | 2026-08-31 post-MCF retune (docs/findings/dispatch-recalibration-post-mcf-2026-08-31.md): floors re-solved from zero after the firm-credit MCF derate (0.9 thermal / 0.95 NGCC) invalidated the 08-28 values. One lever per state (NGCC or hard coal), balance-point target, secant; AR/FL/MS hand-interpolated on coal_err=gas_err (0.7/0.5/0.854). Source: qc/calibration/bgdpbes_0831_round3.csv + the finding doc final-floor table. RESTORED 2026-09-01 after the 08:36 InputData sync wiped the run trees (docs/findings/bau-0901-floor-revert-2026-09-01.md); VT excluded throughout (bad distributed-solar inputs).
PA | petroleum | 0.1295 | PA¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 286.9 GWh / (cap 1319.2 MW x CF 0.1918 x 8760) = 0.1295
RI | petroleum | 1 | RI¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 67.4 GWh / (cap 7.1 MW x CF 0.1096 x 8760) = 9.8839 -- CLIPPED at 1.0; 67.4 GWh of this burns at units whose capacity BHRaSYC books under another row, so it is unreachable
SC | natural gas combined cycle | 0.766 | SC¦natural gas combined cycle | 2026-09-02 cross-state dispatch retune, rounds 1-6 on the bau-0902 basis (Olivia's alignment directive: no opposite-sign coal/gas splits; hydro/wind/solar within 1-2% unless a very small share; both-low/both-high accepted where total generation is short/over). Levers: NGCC/NGST/hard-coal/peaker 2025 guarantee floors read from the run tree after round 6; TN/WY/MT hydro via HYECFCA (hyecfca_retune_2026-09-02.csv). MT: peaker guarantee 1.0 -> 0 (per-state exception to the uniform must-run peaker, K14) and hard-coal floor removed (coal economic). LA: NGST 0.5 is a TRADEOFF -- coal +19.6% -> +8.0% but solar -7.4% -> -16.2% (crowding); revert to 0 to trade back. Round CSVs: qc/calibration/dispatch_retune_0902_round{1..6}.csv. All other states carried forward unchanged.
SC | petroleum | 0.4928 | SC¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 109.0 GWh / (cap 237.4 MW x CF 0.1063 x 8760) = 0.4928
SD | hard coal | 0.8 | SD¦hard coal | 2026-09-02 cross-state dispatch retune, rounds 1-6 on the bau-0902 basis (Olivia's alignment directive: no opposite-sign coal/gas splits; hydro/wind/solar within 1-2% unless a very small share; both-low/both-high accepted where total generation is short/over). Levers: NGCC/NGST/hard-coal/peaker 2025 guarantee floors read from the run tree after round 6; TN/WY/MT hydro via HYECFCA (hyecfca_retune_2026-09-02.csv). MT: peaker guarantee 1.0 -> 0 (per-state exception to the uniform must-run peaker, K14) and hard-coal floor removed (coal economic). LA: NGST 0.5 is a TRADEOFF -- coal +19.6% -> +8.0% but solar -7.4% -> -16.2% (crowding); revert to 0 to trade back. Round CSVs: qc/calibration/dispatch_retune_0902_round{1..6}.csv. All other states carried forward unchanged.
SD | hydro | 0.75 | SD¦hydro | hydro exception: kept below the 0.90 default by decision 2026-08-13 -- 0.90 pinned SD hydro at +10.45% vs EIA-923 2025 (0.90 x SD potential).
SD | petroleum | 0.0298 | SD¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 7.4 GWh / (cap 207.3 MW x CF 0.1363 x 8760) = 0.0298
TN | hard coal | 0.242 | TN¦hard coal | 2026-09-02 cross-state dispatch retune, rounds 1-6 on the bau-0902 basis (Olivia's alignment directive: no opposite-sign coal/gas splits; hydro/wind/solar within 1-2% unless a very small share; both-low/both-high accepted where total generation is short/over). Levers: NGCC/NGST/hard-coal/peaker 2025 guarantee floors read from the run tree after round 6; TN/WY/MT hydro via HYECFCA (hyecfca_retune_2026-09-02.csv). MT: peaker guarantee 1.0 -> 0 (per-state exception to the uniform must-run peaker, K14) and hard-coal floor removed (coal economic). LA: NGST 0.5 is a TRADEOFF -- coal +19.6% -> +8.0% but solar -7.4% -> -16.2% (crowding); revert to 0 to trade back. Round CSVs: qc/calibration/dispatch_retune_0902_round{1..6}.csv. All other states carried forward unchanged.
TN | petroleum | 0.495 | TN¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 126.9 GWh / (cap 470.4 MW x CF 0.0622 x 8760) = 0.4950
TX | hard coal | 0.051155 | TX¦hard coal | 2026-08-31 post-MCF retune (docs/findings/dispatch-recalibration-post-mcf-2026-08-31.md): floors re-solved from zero after the firm-credit MCF derate (0.9 thermal / 0.95 NGCC) invalidated the 08-28 values. One lever per state (NGCC or hard coal), balance-point target, secant; AR/FL/MS hand-interpolated on coal_err=gas_err (0.7/0.5/0.854). Source: qc/calibration/bgdpbes_0831_round3.csv + the finding doc final-floor table. RESTORED 2026-09-01 after the 08:36 InputData sync wiped the run trees (docs/findings/bau-0901-floor-revert-2026-09-01.md); VT excluded throughout (bad distributed-solar inputs).
TX | petroleum | 0.1817 | TX¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 188.6 GWh / (cap 619.3 MW x CF 0.1913 x 8760) = 0.1817
UT | hard coal | 0.92574 | UT¦hard coal | 2026-08-31 post-MCF retune (docs/findings/dispatch-recalibration-post-mcf-2026-08-31.md): floors re-solved from zero after the firm-credit MCF derate (0.9 thermal / 0.95 NGCC) invalidated the 08-28 values. One lever per state (NGCC or hard coal), balance-point target, secant; AR/FL/MS hand-interpolated on coal_err=gas_err (0.7/0.5/0.854). Source: qc/calibration/bgdpbes_0831_round3.csv + the finding doc final-floor table. RESTORED 2026-09-01 after the 08:36 InputData sync wiped the run trees (docs/findings/bau-0901-floor-revert-2026-09-01.md); VT excluded throughout (bad distributed-solar inputs).
UT | petroleum | 0.6289 | UT¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 31.1 GWh / (cap 27.8 MW x CF 0.2029 x 8760) = 0.6289
VA | hard coal | 0.41249 | VA¦hard coal | 2026-08-31 post-MCF retune (docs/findings/dispatch-recalibration-post-mcf-2026-08-31.md): floors re-solved from zero after the firm-credit MCF derate (0.9 thermal / 0.95 NGCC) invalidated the 08-28 values. One lever per state (NGCC or hard coal), balance-point target, secant; AR/FL/MS hand-interpolated on coal_err=gas_err (0.7/0.5/0.854). Source: qc/calibration/bgdpbes_0831_round3.csv + the finding doc final-floor table. RESTORED 2026-09-01 after the 08:36 InputData sync wiped the run trees (docs/findings/bau-0901-floor-revert-2026-09-01.md); VT excluded throughout (bad distributed-solar inputs).
VA | petroleum | 0.818 | VA¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 639.6 GWh / (cap 737.6 MW x CF 0.1210 x 8760) = 0.8180
VT | petroleum | 0.0322 | VT¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 3.9 GWh / (cap 126.0 MW x CF 0.1096 x 8760) = 0.0322
WA | hard coal | 0.91284 | WA¦hard coal | 2026-09-02 WA gas touch-up on the bau-0901 evening basis (Olivia's request: guarantee gas to within 2%, eating hydro dispatch): NGCC 2025 floor solved by two-point secant (0 -> probe 0.943604 -> 0.35612), lands gas -1.66% / hydro +0.30% / coal +1.71%, wind-solar untouched. Coal floor 0.912841 unchanged from the 09-01 round. Target was -1.5%, not 0, leaving room for the registered grid-sold-CHP share of the EIA gas benchmark (task 9 decision). Run tree also re-carries the Centralia BCRbQ 670 MW @2028 (found wiped, all-zeros, when this round started; upstream fix still O68). All other states carried forward from bgd_tune_results_2026-09-01.csv unchanged.
WA | natural gas combined cycle | 0.35612 | WA¦natural gas combined cycle | 2026-09-02 WA gas touch-up on the bau-0901 evening basis (Olivia's request: guarantee gas to within 2%, eating hydro dispatch): NGCC 2025 floor solved by two-point secant (0 -> probe 0.943604 -> 0.35612), lands gas -1.66% / hydro +0.30% / coal +1.71%, wind-solar untouched. Coal floor 0.912841 unchanged from the 09-01 round. Target was -1.5%, not 0, leaving room for the registered grid-sold-CHP share of the EIA gas benchmark (task 9 decision). Run tree also re-carries the Centralia BCRbQ 670 MW @2028 (found wiped, all-zeros, when this round started; upstream fix still O68). All other states carried forward from bgd_tune_results_2026-09-01.csv unchanged.
WA | hydro | 0 | WA¦hydro | hydro exception (staff 2026-07-22): guarantee removed; WA at the $80 HOC cap still over-dispatched, so hydro is the pure least-cost residual.
WA | petroleum | 1 | WA¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 12.1 GWh / (cap 7.9 MW x CF 0.1189 x 8760) = 1.4653 -- CLIPPED at 1.0; 11.4 GWh of this burns at units whose capacity BHRaSYC books under another row, so it is unreachable
WI | natural gas combined cycle | 0.4879 | WI¦natural gas combined cycle | 2026-09-01 touch-up round on the noon bau-0901 basis (docs/findings/bgdpbes-touchup-2026-09-01.md): SD/OH coal and FL/WI NGCC floors re-solved by two-point secant from the 08-31 values (FL hand-interpolated on coal_err=gas_err, the 0831-doc blind-spot case); WA re-enters the calibration with the Centralia BCRbQ retirement moved to the 2026 column (RUN-TREE edit, upstream fix owed under O68) and HOC 55, coal floor solved in the floored regime. WA floor is only meaningful with the BCRbQ fix deployed alongside. All other states carried forward from bgd_tune_results_2026-08-31.csv unchanged; VT excluded throughout.
WI | petroleum | 0.2692 | WI¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 106.5 GWh / (cap 515.4 MW x CF 0.0876 x 8760) = 0.2692
WV | hard coal | 1 | WV¦hard coal | 2026-08-31 post-MCF retune (docs/findings/dispatch-recalibration-post-mcf-2026-08-31.md): floors re-solved from zero after the firm-credit MCF derate (0.9 thermal / 0.95 NGCC) invalidated the 08-28 values. One lever per state (NGCC or hard coal), balance-point target, secant; AR/FL/MS hand-interpolated on coal_err=gas_err (0.7/0.5/0.854). Source: qc/calibration/bgdpbes_0831_round3.csv + the finding doc final-floor table. RESTORED 2026-09-01 after the 08:36 InputData sync wiped the run trees (docs/findings/bau-0901-floor-revert-2026-09-01.md); VT excluded throughout (bad distributed-solar inputs).
WV | petroleum | 1 | WV¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 141.9 GWh / (cap 11.0 MW x CF 0.2921 x 8760) = 5.0428 -- CLIPPED at 1.0; 141.6 GWh of this burns at units whose capacity BHRaSYC books under another row, so it is unreachable
WY | natural gas steam turbine | 0.251 | WY¦natural gas steam turbine | 2026-09-02 cross-state dispatch retune, rounds 1-6 on the bau-0902 basis (Olivia's alignment directive: no opposite-sign coal/gas splits; hydro/wind/solar within 1-2% unless a very small share; both-low/both-high accepted where total generation is short/over). Levers: NGCC/NGST/hard-coal/peaker 2025 guarantee floors read from the run tree after round 6; TN/WY/MT hydro via HYECFCA (hyecfca_retune_2026-09-02.csv). MT: peaker guarantee 1.0 -> 0 (per-state exception to the uniform must-run peaker, K14) and hard-coal floor removed (coal economic). LA: NGST 0.5 is a TRADEOFF -- coal +19.6% -> +8.0% but solar -7.4% -> -16.2% (crowding); revert to 0 to trade back. Round CSVs: qc/calibration/dispatch_retune_0902_round{1..6}.csv. All other states carried forward unchanged.
WY | natural gas combined cycle | 1 | WY¦natural gas combined cycle | 2026-09-02 cross-state dispatch retune, rounds 1-6 on the bau-0902 basis (Olivia's alignment directive: no opposite-sign coal/gas splits; hydro/wind/solar within 1-2% unless a very small share; both-low/both-high accepted where total generation is short/over). Levers: NGCC/NGST/hard-coal/peaker 2025 guarantee floors read from the run tree after round 6; TN/WY/MT hydro via HYECFCA (hyecfca_retune_2026-09-02.csv). MT: peaker guarantee 1.0 -> 0 (per-state exception to the uniform must-run peaker, K14) and hard-coal floor removed (coal economic). LA: NGST 0.5 is a TRADEOFF -- coal +19.6% -> +8.0% but solar -7.4% -> -16.2% (crowding); revert to 0 to trade back. Round CSVs: qc/calibration/dispatch_retune_0902_round{1..6}.csv. All other states carried forward unchanged.
WY | petroleum | 1 | WY¦petroleum | ALL YEARS (2025-only rule exception, Olivia 2026-08-26): oil-fired gen 2025 52.7 GWh / (cap 4.7 MW x CF 0.0970 x 8760) = 13.1908 -- CLIPPED at 1.0; 52.4 GWh of this burns at units whose capacity BHRaSYC books under another row, so it is unreachable

## Fleet
FLEET SCREEN -- start-year (2025) electricity generation capacity by state and tech, MW
Why: the four coal/gas guarantees are 2025-only, so a guarantee on a tech with no 2025 fleet is inert AND misleading. The BGDPbES tab multiplies those four rows by the has_fleet flag at the bottom of this tab.
SOURCE AND PROVENANCE
source file pattern | state-eps-data/<ST>/elec/BHRaSYC/BHRaSYC-StartYearCapacities.csv
handling | summed across all Vintage columns per tech row; verbatim otherwise
states read | 48
accessed | 2026-09-02
note | BHRaSYC is generated outside this repo, so it is read from the deployed tree. Not circular: it is a different variable, so no BGDPbES value can be fed back into a rebuild.
PER-FILE PROVENANCE
state | bytes | sha256 (12) | vintage cols | tech rows
AL | 34670 | aa554e6117ee | 210 | 24
AR | 34605 | b9fb75c5c686 | 210 | 24
AZ | 34670 | 221490253617 | 210 | 24
CA | 34935 | 7af171e7c975 | 210 | 24
CO | 34660 | 27074de39c39 | 210 | 24
CT | 34599 | f8a2189f707c | 210 | 24
DE | 34554 | a9513e0f983f | 210 | 24
FL | 34777 | 013ebcbe3215 | 210 | 24
GA | 34671 | 52641aea61a6 | 210 | 24
IA | 34659 | f3053fb669a5 | 210 | 24
ID | 34620 | 28c133c4ac92 | 210 | 24
IL | 34671 | 96e03f983a73 | 210 | 24
IN | 34660 | eb94d066a605 | 210 | 24
KS | 34646 | af73cb9ac8d8 | 210 | 24
KY | 34608 | 54617d7f1cf7 | 210 | 24
LA | 34654 | 97ea1e121763 | 210 | 24
MA | 34614 | 02d1adb996c5 | 210 | 24
MD | 34589 | 92d33475678b | 210 | 24
ME | 34591 | 0d43525d6653 | 210 | 24
MI | 34692 | 414ffa512a45 | 210 | 24
MN | 34682 | fb64d8dc11c1 | 210 | 24
MO | 34662 | 14ee25b3e9bc | 210 | 24
MS | 34585 | 627c99019e97 | 210 | 24
MT | 34601 | df41a694e011 | 210 | 24
NC | 34691 | 25e1cd278c1f | 210 | 24
ND | 34582 | a510024c4ee1 | 210 | 24
NE | 34597 | 2c34eed6bc08 | 210 | 24
NH | 34556 | 365038811b86 | 210 | 24
NJ | 34626 | 43f1cc176e62 | 210 | 24
NM | 34609 | 7d01287a81f6 | 210 | 24
NV | 34630 | 7145cb1c943c | 210 | 24
NY | 34766 | 2f31d6940c58 | 210 | 24
OH | 34644 | 2c58425dbb4f | 210 | 24
OK | 34673 | 5bb261f5cc3e | 210 | 24
OR | 34650 | 015ee80dda33 | 210 | 24
PA | 34720 | d645d357a139 | 210 | 24
RI | 34540 | 44a8b4ab997b | 210 | 24
SC | 34650 | d2c35df314e6 | 210 | 24
SD | 34580 | dd863a4a5b87 | 210 | 24
TN | 34629 | 2603469637eb | 210 | 24
TX | 34930 | 0ac3e67f11c7 | 210 | 24
UT | 34591 | 1dacb1bab934 | 210 | 24
VA | 34649 | 7065cdbd1593 | 210 | 24
VT | 34537 | 7003bb27e23e | 210 | 24
WA | 34708 | fca4d6d152ca | 210 | 24
WI | 34654 | e47606ad254b | 210 | 24
WV | 34573 | cc6e53f108b9 | 210 | 24
WY | 34596 | 13185dd4cac1 | 210 | 24
START-YEAR CAPACITY BY STATE AND TECH (MW)
state | hard coal | natural gas steam turbine | natural gas combined cycle | nuclear | hydro | onshore wind | solar PV | solar thermal | biomass | geothermal | petroleum | natural gas peaker | lignite | offshore wind | crude oil | heavy or residual fuel oil | municipal solid waste | hard coal w CCS | natural gas combined cycle w CCS | biomass w CCS | lignite w CCS | small modular reactor | hydrogen combustion turbine | hydrogen combined cycle
AL | 4728 | 1696.1 | 11072 | 5452.7 | 3290.6 | 0 | 663.5 | 0 | 6.4 | 0 | 42.6 | 3220.2 | 0 | 0 | 797.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AR | 4729.6 | 656 | 4608.2 | 1821 | 1264.5 | 0 | 1772.46 | 0 | 8.8 | 0 | 9 | 715.6 | 0 | 0 | 280.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AZ | 2936 | 1095 | 10116.1 | 3937 | 2720.6 | 1234.5 | 4730.2 | 295.6 | 27.9 | 0 | 84.7 | 3303.1 | 0 | 0 | 58.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CA | 0 | 3730.7 | 19425.3 | 2240 | 10207.4 | 6428.7 | 21087.25 | 917.8 | 572.9 | 1881.2 | 224 | 11157.1 | 0 | 0 | 3212.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CO | 3786 | 364 | 3219.5 | 0 | 689.4 | 5334.9 | 2349.54 | 0 | 28.7 | 0 | 148.1 | 2862.12 | 0 | 0 | 114.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CT | 0 | 434 | 3835.18 | 2104.2 | 119.2 | 5 | 314.2 | 0 | 39.1 | 0 | 2197.2 | 497.69 | 0 | 0 | 226.85 | 0 | 100.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DE | 410 | 695 | 1496 | 0 | 0 | 0 | 91.9 | 0 | 10 | 0 | 111.1 | 184 | 0 | 0 | 276.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FL | 3564.7 | 5418.9 | 35819.7 | 3666 | 43.5 | 0 | 10942.9 | 0 | 271.8 | 0 | 1594.9 | 8838.2 | 0 | 0 | 1025.1 | 0 | 250.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GA | 5780 | 724 | 8090.8 | 6289 | 1979.9 | 0 | 4999.4 | 0 | 294.3 | 0 | 1014.3 | 7363.7 | 0 | 0 | 1166.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IA | 4392.9 | 470.8 | 1700.7 | 0 | 209.4 | 12864.5 | 676.1 | 0 | 16.2 | 0 | 775.9 | 1364.94 | 0 | 0 | 744.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ID | 0 | 0 | 515.43 | 0 | 2653.76 | 1128.3 | 500 | 0 | 26.4 | 10 | 5.58 | 568.96 | 0 | 0 | 98.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IL | 6356.7 | 28.2 | 5449.2 | 11591.6 | 31.7 | 7872 | 2955 | 0 | 55.2 | 0 | 650 | 10372.1 | 0 | 0 | 817.14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IN | 12721.4 | 640 | 3892.3 | 0 | 69.1 | 3639.1 | 2489.2 | 0 | 33.3 | 0 | 62.8 | 3221.6 | 0 | 0 | 974.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KS | 4694.98 | 800.1 | 247 | 1176.7 | 7 | 9036 | 65.8 | 0 | 9 | 0 | 540.1 | 2722.1 | 0 | 0 | 57.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KY | 8631 | 714 | 1791 | 0 | 1137.4 | 0 | 425.2 | 0 | 18.2 | 0 | 10.8 | 5576.6 | 0 | 0 | 76.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LA | 2121.6 | 4901.1 | 7089.1 | 2051.5 | 192 | 0 | 1052.6 | 0 | 11.1 | 0 | 839 | 1775.8 | 0 | 0 | 4631.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MA | 0 | 0 | 4387.23 | 0 | 265.2 | 85.1 | 1419.13 | 0 | 38.5 | 0 | 2180.7 | 444.9 | 0 | 0 | 442.7 | 0 | 102.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MD | 1273 | 1182.3 | 2716.6 | 1745.2 | 514.9 | 190 | 659.7 | 0 | 16.4 | 0 | 1537.4 | 1625.3 | 0 | 0 | 133.9 | 0 | 115.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ME | 0 | 0 | 1272.17 | 0 | 708.1 | 1029.5 | 829.2 | 0 | 284.8 | 0 | 842.9 | 178 | 0 | 0 | 367.8 | 0 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MI | 5726.5 | 2027.3 | 7622.6 | 4086.5 | 261.6 | 3774.3 | 1157 | 0 | 303.6 | 0 | 373.9 | 3855.6 | 0 | 0 | 519.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MN | 3004 | 175.3 | 2483 | 1657 | 194.2 | 4891.5 | 1596.66 | 0 | 65.6 | 0 | 727.3 | 2796.67 | 0 | 0 | 527.3 | 0 | 69.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MO | 8539.2 | 185.99 | 1889.2 | 1190 | 548.5 | 2392.9 | 468.77 | 0 | 14 | 0 | 1038.23 | 3377.16 | 0 | 0 | 117.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MS | 1004 | 1486.5 | 8450.7 | 1390.3 | 0 | 184.5 | 1219.7 | 0 | 1.6 | 0 | 9 | 1360.4 | 440 | 0 | 362.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MT | 1625 | 0 | 0 | 0 | 2833.98 | 1889.62 | 177 | 0 | 3.2 | 0 | 52 | 553.6 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NC | 5561 | 3248 | 5579 | 5149.6 | 2005.8 | 397 | 6726.2 | 0 | 142.6 | 0 | 425.7 | 6332.3 | 0 | 0 | 543.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ND | 1142.2 | 96.9 | 0 | 0 | 510 | 4514 | 0 | 0 | 0 | 0 | 54.61 | 649.2 | 2670.4 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NE | 3756.9 | 378.3 | 338.9 | 768.5 | 278.7 | 3516.9 | 136.5 | 0 | 10.85 | 0 | 373.7 | 1224.8 | 0 | 0 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NH | 533.9 | 400.2 | 1228.5 | 1250 | 505.8 | 211.9 | 2.4 | 0 | 205.9 | 0 | 82.1 | 0 | 0 | 0 | 23.6 | 0 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NJ | 0 | 0 | 8212.5 | 3456.7 | 12.3 | 7.6 | 1055.94 | 0 | 44.3 | 0 | 270 | 2529.9 | 0 | 0 | 433.14 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NM | 1540 | 721 | 1429.4 | 0 | 82.7 | 3995.5 | 2321.9 | 0 | 6.4 | 8.6 | 17 | 977.6 | 0 | 0 | 98.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NV | 740.4 | 334 | 5703 | 0 | 1051.7 | 150 | 4987 | 178.5 | 9.8 | 662.5 | 6 | 1621.6 | 0 | 0 | 165.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NY | 0 | 9633.75 | 9823.1 | 3330.4 | 4546.3 | 2733.6 | 2651.6 | 0 | 115.3 | 0 | 3245 | 2396.48 | 0 | 130 | 924.91 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OH | 6620.5 | 23 | 10506.1 | 2134 | 101.9 | 1063.3 | 3226 | 0 | 41.7 | 0 | 630.2 | 5741.9 | 0 | 0 | 295.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OK | 3258.9 | 5320.5 | 7299.7 | 0 | 832.4 | 12748.2 | 173.5 | 0 | 2.8 | 0 | 35.9 | 1811.96 | 0 | 0 | 170.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OR | 0 | 0 | 3394.5 | 0 | 8264.14 | 3970.4 | 1051.7 | 0 | 85.6 | 19.5 | 0 | 353.2 | 0 | 0 | 219.1 | 0 | 11.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PA | 5346.5 | 5621.9 | 18682.55 | 9896 | 929.5 | 1552.6 | 861 | 0 | 100.1 | 0 | 1319.2 | 1933 | 0 | 0 | 896.6 | 0 | 170.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RI | 0 | 0 | 1735.2 | 0 | 2.7 | 43.5 | 418.5 | 0 | 40.1 | 0 | 7.1 | 0 | 0 | 29.3 | 42.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SC | 4754 | 760 | 3252 | 6600.3 | 1293 | 0 | 1643.6 | 0 | 88.1 | 0 | 237.4 | 2543.79 | 0 | 0 | 409.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SD | 477.28 | 0 | 295 | 0 | 1598 | 3450.3 | 209 | 0 | 0 | 0 | 207.35 | 973.59 | 0 | 0 | 14.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TN | 4593 | 0 | 2455.1 | 4522.7 | 2608.6 | 2.1 | 594.95 | 0 | 14.2 | 0 | 470.4 | 3325.6 | 0 | 0 | 402.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TX | 13877.6 | 15563.5 | 39130 | 4980 | 712.1 | 41962.9 | 22368.3 | 0 | 172.9 | 0 | 619.3 | 10913.86 | 2406 | 0 | 7686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
UT | 4581 | 237.5 | 1830 | 0 | 246.7 | 389.7 | 2185.7 | 0.1 | 10.6 | 70.7 | 27.8 | 552.2 | 0 | 0 | 135.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VA | 1487.1 | 515 | 8910.1 | 3568 | 864.1 | 0 | 4677.41 | 0 | 291.6 | 0 | 737.6 | 4198 | 0 | 12 | 561.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
VT | 0 | 0 | 0 | 0 | 331 | 150.2 | 155.2 | 0 | 79.5 | 0 | 126 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WA | 670 | 0 | 2636.6 | 1151 | 21513 | 3374.9 | 268.3 | 0 | 54.5 | 0 | 7.9 | 623.8 | 0 | 0 | 332.6 | 0 | 22.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WI | 4701.8 | 382.6 | 3426.8 | 1185.3 | 392 | 813.25 | 2100.6 | 0 | 169.1 | 0 | 515.4 | 3308.95 | 0 | 0 | 412.59 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WV | 12542.5 | 0 | 0 | 0 | 237.8 | 855.2 | 124.4 | 0 | 3.2 | 0 | 11 | 1088.3 | 0 | 0 | 218.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WY | 4928 | 1317 | 94 | 0 | 307.1 | 3603.9 | 242 | 0 | 0 | 0 | 4.7 | 145 | 0 | 0 | 203.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CHECK: 48-state total (MW) -- an identity, so any nonzero difference is real
sum of state rows | 167137.16 | 71978.44 | 283151.06 | 98391.2 | 79169.28 | 151487.37 | 120824.11 | 1392 | 3846.15 | 2652.5 | 24502.87 | 131180.47 | 5516.4 | 171.3 | 31349.39 | 0 | 979.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ACTIVE STATE FLEET (About!B2) -- read by the BGDPbES tab
tech | start-year MW | has_fleet (1 = state has a 2025 fleet)
hard coal | 4728 | 1
natural gas steam turbine | 1696.1 | 1
natural gas combined cycle | 11072 | 1
nuclear | 5452.7 | 1
hydro | 3290.6 | 1
onshore wind | 0 | 0
solar PV | 663.5 | 1
solar thermal | 0 | 0
biomass | 6.4 | 1
geothermal | 0 | 0
petroleum | 42.6 | 1
natural gas peaker | 3220.2 | 1
lignite | 0 | 0
offshore wind | 0 | 0
crude oil | 797.6 | 1
heavy or residual fuel oil | 0 | 0
municipal solid waste | 0 | 0
hard coal w CCS | 0 | 0
natural gas combined cycle w CCS | 0 | 0
biomass w CCS | 0 | 0
lignite w CCS | 0 | 0
small modular reactor | 0 | 0
hydrogen combustion turbine | 0 | 0
hydrogen combined cycle | 0 | 0

## BGDPbES
BAU Guaranteed Dispatch (dimensionless) | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
hard coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
natural gas steam turbine | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
natural gas combined cycle | 0 | 0 | 0 | 0 | 0.3062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
nuclear | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
hydro | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
onshore wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
solar PV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
solar thermal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
biomass | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
geothermal | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
petroleum | 0.4912 | 0.4912 | 0.4912 | 0.4912 | 0.4912 | 0.4912 | 0.4912 | 0.4912 | 0.4912 | 0.4912 | 0.4912 | 0.4912 | 0.4912 | 0.4912 | 0.4912 | 0.4912 | 0.4912 | 0.4912 | 0.4912 | 0.4912 | 0.4912 | 0.4912 | 0.4912 | 0.4912 | 0.4912 | 0.4912 | 0.4912 | 0.4912 | 0.4912 | 0.4912
natural gas peaker | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
lignite | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
offshore wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
crude oil | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
heavy or residual fuel oil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
municipal solid waste | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
hard coal w CCS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
natural gas combined cycle w CCS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
biomass w CCS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
lignite w CCS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
small modular reactor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
hydrogen combustion turbine | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
hydrogen combined cycle | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0